CALCULATION REPORT - ANCHORAGE AND LAP LENGTHS

PJR-2026-003_WAREHOUSE (STEAM BOILER)

Document control

| Item | Value |
| --- | --- |
| Document number | WH-STR-CR-001 |
| Project | PJR-2026-003 WAREHOUSE (STEAM BOILER) |
| Client | Mr. XXX |
| Stage | FOR APPROVAL |
| Revision / date | R00 / 13-OCT-2026 |
| Design basis | PJR-2026-003 design basis, status DRAFT |
| National Annex | CEN_RECOMMENDED (Cambodia) |
| Prepared by | P.LIHENG |
| Checked by |  |
| Approved by |  |

Scope: this report covers ONE check only (EN 1992-1-1 bond/anchorage lengths) and reconciles it with sheet WH-STR-SD-004. It is not a complete structural design calculation. Report standard 10 is not yet authored; format is PROPOSED.

A.  SCOPE

Anchorage and basic lap lengths for C30/37 concrete with fyk = 390 MPa are calculated to EN 1992-1-1 and compared with the table in section C of drawing WH-STR-SD-004 (R00).

B.  DESIGN CODES AND NATIONAL ANNEX

Design codes (from design basis)

| Standard | Generation | Edition | Used for |
| --- | --- | --- | --- |
| EN 1990 | NOT RECORDED | NOT RECORDED | Basis of structural design |
| EN 1991-1-1 | NOT RECORDED | NOT RECORDED | Self-weight, imposed loads |
| EN 1991-1-3 | NOT RECORDED | NOT RECORDED | Snow |
| EN 1991-1-4 | NOT RECORDED | NOT RECORDED | Wind |
| EN 1992-1-1 | NOT RECORDED | NOT RECORDED | Concrete structures (RC) |
| EN 1993-1-1 | NOT RECORDED | NOT RECORDED | Steel - general rules |
| EN 1993-1-3 | NOT RECORDED | NOT RECORDED | Cold-formed members (purlins/girts) |
| EN 1993-1-5 | NOT RECORDED | NOT RECORDED | Plated structural elements |
| EN 1993-1-8 | NOT RECORDED | NOT RECORDED | Joints |
| EN 1997-1 | NOT RECORDED | NOT RECORDED | Geotechnical design |

Mixed 1st/2nd generation Eurocodes: User decision (P.Liheng, 14-OCT-2026): 1st and 2nd generation Eurocode parts may be combined on this project. The generation of each part must still be recorded per standard entry; compatibility of each combination is for the engineer to confirm.

National Annex: CEN_RECOMMENDED. Per SD-003: CEN recommended values used (no National Annex for Cambodia); local authority requirements apply where more onerous. Confirmed by user (P.Liheng) 14-OCT-2026.

C.  MATERIALS

Materials (from design basis)

| Id | Element | Specification | Status | Source |
| --- | --- | --- | --- | --- |
| M-CONC-STUMP | Stump columns / stiffener columns | C30/37 XC1/XC4 | confirmed | SD-004 A |
| M-CONC-PILE | Pile caps / tie beams / ground beams | C30/37 XC2 | confirmed | SD-004 A |
| M-REBAR | Reinforcement | fyk = 390 MPa deformed bars, grade 390 | confirmed | SD-004 A |
| M-STEEL-MAIN | Plates / welded sections / hot-rolled | S355JR (EN 10025-2) | confirmed | SD-005 A |
| M-BOLTS | Structural bolts | Class 8.8 / 10.9 (EN 14399-3 HRPV preloaded where noted) | confirmed | SD-005 A |

D.  ANCHORAGE AND LAP LENGTHS

CALC-ANCH-001  Anchorage and lap lengths, C30/37 with fyk = 390 MPa

Code reference: EN 1992-1-1 3.1.6, 8.4.2, 8.4.3

Inputs

| Input | Value | Unit | Source |
| --- | --- | --- | --- |
| concrete class | C30/37 | - | design basis M-CONC-PILE (SD-004 section A) |
| fyk | 390.0 | MPa | design basis M-REBAR (SD-004 section A) |
| gamma_c | 1.5 | - | EN 1992-1-1 Table 2.1N (CEN recommended) |
| gamma_s | 1.15 | - | EN 1992-1-1 Table 2.1N (CEN recommended) |
| alpha_ct | 1.0 | - | EN 1992-1-1 3.1.6(2)P (CEN recommended) |
| fctk,0.05 | 2.0 | MPa | EN 1992-1-1 Table 3.1 |

Calculation

| Step | Formula | Substitution | Result | Unit |
| --- | --- | --- | --- | --- |
| Design tensile strength | fctd = alpha_ct * fctk,0.05 / gamma_c | 1.0 * 2.0 / 1.5 | 1.333 | MPa |
| Bond stress, good conditions | fbd = 2.25 * eta1 * eta2 * fctd (eta1=1.0, eta2=1.0) | 2.25 * 1.0 * 1.0 * 1.333 | 3.0 | MPa |
| Bond stress, poor conditions | fbd = 2.25 * eta1 * eta2 * fctd (eta1=0.7, eta2=1.0) | 2.25 * 0.7 * 1.0 * 1.333 | 2.1 | MPa |
| Design steel stress | sigma_sd = fyd = fyk / gamma_s | 390 / 1.15 | 339.1 | MPa |

Results (unrounded; tabulated fctk,0.05)

| Bar diameter (mm) | 10 | 12 | 16 | 20 | 25 |
| --- | --- | --- | --- | --- | --- |
| lb,rqd good bond (mm) | 283 | 339 | 452 | 565 | 706 |
| lb,rqd poor bond (mm) | 404 | 484 | 646 | 808 | 1009 |
| lap l0 good, 50% lapped (mm) | 424 | 509 | 678 | 848 | 1060 |

Scope limits: Basic required anchorage length only (alpha1-alpha5 = 1.0, lb,min not applied); lap = alpha6 * lb,rqd with alpha6 = 1.5. Straight bars.

Reconciliation with SD-004 section C table (WH-STR-SD-004 as corrected: mandrel 20 mm = 140, 25 mm = 175)

| Bar diameter (mm) | 10 | 12 | 16 | 20 | 25 |
| --- | --- | --- | --- | --- | --- |
| lbd good bond - drawing | 280 | 335 | 445 | 560 | 700 |
| lbd good bond - calc, drawing basis (fctk,0.05 = 2.03) | 278 | 334 | 445 | 557 | 696 |
| deviation (drawing - calc), mm | +2 | +1 | +0 | +3 | +4 |
| lbd good bond - calc, Table 3.1 (fctk,0.05 = 2.0) | 283 | 339 | 452 | 565 | 707 |
| deviation (drawing - calc), mm | -3 | -4 | -7 | -5 | -7 |
| lbd poor bond - drawing | 400 | 480 | 640 | 800 | 1000 |
| lbd poor bond - calc, drawing basis (fctk,0.05 = 2.03) | 398 | 477 | 636 | 796 | 994 |
| deviation (drawing - calc), mm | +2 | +3 | +4 | +4 | +6 |
| lbd poor bond - calc, Table 3.1 (fctk,0.05 = 2.0) | 404 | 484 | 646 | 807 | 1009 |
| deviation (drawing - calc), mm | -4 | -4 | -6 | -7 | -9 |
| lap l0 good (<=50% lapped) - drawing | 420 | 505 | 670 | 840 | 1050 |
| lap l0 good (<=50% lapped) - calc, drawing basis (fctk,0.05 = 2.03) | 418 | 501 | 668 | 835 | 1044 |
| deviation (drawing - calc), mm | +2 | +4 | +2 | +5 | +6 |
| lap l0 good (<=50% lapped) - calc, Table 3.1 (fctk,0.05 = 2.0) | 424 | 509 | 678 | 848 | 1060 |
| deviation (drawing - calc), mm | -4 | -4 | -8 | -8 | -10 |

Drawing basis: fctk,0.05 = 0.7*fctm = 2.03 MPa -> fbd = 3.04 MPa.

Drawing values agree with the calculation on the drawing's own basis within larger of 5 mm or 1 %: YES. Against the tabulated fctk,0.05 = 2.0 MPa the drawing values are shorter by up to 1.55 % (10 mm).

Verification status: CROSS-CHECKED against issued drawing; not independently reviewed by an engineer. Method: Reconciled with the SD-004 table (see reconciliation) and unit tests against hand values in tests/test_phase4.py.

E.  CONCLUSIONS AND LIMITATIONS

The anchorage and lap lengths on SD-004 reproduce from the EN 1992-1-1 expressions on the drawing's own basis (fbd = 3.04 MPa), within the tolerance stated in the reconciliation. They are slightly shorter (about 1 to 1.6 %, see the reconciliation table) than values from the tabulated fctk,0.05 = 2.0 MPa; the engineer should decide which basis governs.

The mandrel-diameter row of SD-004 as issued (R00) gave 80 and 100 mm for 20 mm and 25 mm bars, which conflicts with EN 1992-1-1 8.3(1) and with the sheet's own note (7 phi above 16 mm = 140 and 175 mm). The corrected values are used in this calculation and have been applied to the sheet file; the engineer should confirm the sheet revision that carries the correction.

Workbook WH-STR-WB-001_R00.xlsx implements the same check with live formulas. Its results were tied out to this report's results file (CALC-ANCH-001) by tools/xlsxgen/verify_workbook.py, and it carries 8 hand-calculated checks.

Only basic required lengths are checked (alpha1-alpha5 = 1.0, no lb,min). The check was cross-checked against the issued drawing and unit tests; it has not been reviewed by an authorised engineer.

F.  ASSUMPTIONS TO BE CONFIRMED

| Id | Open item (from design basis) |
| --- | --- |
| F1 | Foundation - precast square driven piles 300x300, L=7.0 m; soil investigation and pile load tests required |
| F2 | Boiler / piping / crane / hoist and any platform loads not included |
| F3 | Openings (doors, louvres, flue) not shown |
| F4 | Terrain category II and no shielding, site altitude < 100 m |
| F5 | Longitudinal (grid A/B) wind sway by braced bays - confirm |
| F6 | Purlins/girts cold-formed - supplier verification for loads in SD-108 |
| F7 | Client name is a placeholder |
| F8 | Eave sway limit h/100 = 120 mm - confirm with cladding supplier |