STRUCTURAL SPECIFICATION (SEED DRAFT)

PJR-2026-003_WAREHOUSE (STEAM BOILER)

Document control

| Item | Value |
| --- | --- |
| Document number | WH-STR-SP-001 |
| Project | PJR-2026-003 WAREHOUSE (STEAM BOILER) |
| Client | Mr. XXX |
| Stage | FOR APPROVAL |
| Revision / date | R00 / 13-OCT-2026 |
| Design basis | PJR-2026-003 design basis, status DRAFT |
| National Annex | CEN_RECOMMENDED (Cambodia) |
| Prepared by | P.LIHENG |
| Checked by |  |
| Approved by |  |

Seed draft generated from the issued WH-STR-SD R00 notes and the design basis. Specification standard 07 is not yet authored; format is PROPOSED.

1  GENERAL REQUIREMENTS

1.1	The structure shall be designed to the Eurocodes listed below using CEN recommended parameter values; local authority requirements shall apply where more onerous. [DB: national_annex; SD-003 B]

Design codes (from design basis)

| Standard | Generation | Edition | Used for |
| --- | --- | --- | --- |
| EN 1990 | NOT RECORDED | NOT RECORDED | Basis of structural design |
| EN 1991-1-1 | NOT RECORDED | NOT RECORDED | Self-weight, imposed loads |
| EN 1991-1-3 | NOT RECORDED | NOT RECORDED | Snow |
| EN 1991-1-4 | NOT RECORDED | NOT RECORDED | Wind |
| EN 1992-1-1 | NOT RECORDED | NOT RECORDED | Concrete structures (RC) |
| EN 1993-1-1 | NOT RECORDED | NOT RECORDED | Steel - general rules |
| EN 1993-1-3 | NOT RECORDED | NOT RECORDED | Cold-formed members (purlins/girts) |
| EN 1993-1-5 | NOT RECORDED | NOT RECORDED | Plated structural elements |
| EN 1993-1-8 | NOT RECORDED | NOT RECORDED | Joints |
| EN 1997-1 | NOT RECORDED | NOT RECORDED | Geotechnical design |

Mixed 1st/2nd generation Eurocodes: User decision (P.Liheng, 14-OCT-2026): 1st and 2nd generation Eurocode parts may be combined on this project. The generation of each part must still be recorded per standard entry; compatibility of each combination is for the engineer to confirm.

National Annex: CEN_RECOMMENDED. Per SD-003: CEN recommended values used (no National Annex for Cambodia); local authority requirements apply where more onerous. Confirmed by user (P.Liheng) 14-OCT-2026.

1.2	Concrete work shall be executed to EN 13670. [SD-004 notes]  [SEED - verify]

1.3	Steelwork fabrication and erection shall be to EN 1090-2, execution class EXC2. [SD-005 C]  [SEED - verify]

2  MATERIALS

Materials (from design basis)

| Id | Element | Specification | Status | Source |
| --- | --- | --- | --- | --- |
| M-CONC-STUMP | Stump columns / stiffener columns | C30/37 XC1/XC4 | confirmed | SD-004 A |
| M-CONC-PILE | Pile caps / tie beams / ground beams | C30/37 XC2 | confirmed | SD-004 A |
| M-REBAR | Reinforcement | fyk = 390 MPa deformed bars, grade 390 | confirmed | SD-004 A |
| M-STEEL-MAIN | Plates / welded sections / hot-rolled | S355JR (EN 10025-2) | confirmed | SD-005 A |
| M-BOLTS | Structural bolts | Class 8.8 / 10.9 (EN 14399-3 HRPV preloaded where noted) | confirmed | SD-005 A |

2.1	Reinforcement shall be deformed bars with characteristic yield strength fyk = 390 MPa. [DB: M-REBAR]

2.2	Structural steel plates and welded sections shall be S355JR to EN 10025-2. [DB: M-STEEL-MAIN]

3  WORKMANSHIP

3.1	Concrete shall be compacted with poker vibrators and wet cured for a minimum of 7 days (EN 13670 curing class 2). [SD-004 E]  [SEED - verify]

3.2	No reinforcing bar shall be rebent on site except as permitted by EN 13670. [SD-004 D]  [SEED - verify]

3.3	No steel erection shall start until the stump columns have achieved 70 % of fck and the anchor bolts have been surveyed. [SD-004 E]  [SEED - verify]

4  QUALITY CONTROL

4.1	Concrete compression testing shall be one set of three cubes per pour or per 50 m3, tested at 7 and 28 days to EN 12390. [SD-004 E]  [SEED - verify]

5  ASSUMPTIONS TO BE CONFIRMED

| Id | Open item (from design basis) |
| --- | --- |
| F1 | Foundation - precast square driven piles 300x300, L=7.0 m; soil investigation and pile load tests required |
| F2 | Boiler / piping / crane / hoist and any platform loads not included |
| F3 | Openings (doors, louvres, flue) not shown |
| F4 | Terrain category II and no shielding, site altitude < 100 m |
| F5 | Longitudinal (grid A/B) wind sway by braced bays - confirm |
| F6 | Purlins/girts cold-formed - supplier verification for loads in SD-108 |
| F7 | Client name is a placeholder |
| F8 | Eave sway limit h/100 = 120 mm - confirm with cladding supplier |